## Sheet1
CWL(CXL)系列舰船用小型离心通风机CWL(CXL)
CWL(CXL) series marine small-sized centrifhgal fan
series marine small-sized centrifhgal fan
概念General CWL(CXL)系列舰船小型离心通风机可输送空气，含有盐雾的海洋空气和含有油雾等腐蚀性空气。本型风机适用于军船与民船上的厨房、厕所、舱壁、公共场所、会议室等的通风换气和各舱室的通风，也适用于陆上化工、冶金等行业的适当场所。 CWL（CXL）型舰船用小型离心通风机如裴勇防爆电机，即可输送易燃、易爆的混合型气体和蒸汽，又能在“危险区”安全工作。 CWL（CXL.）型舰船用小型离心通风机，可配用船用三相微型异步电动机，适用于380V/220V或440V,50/60Hz的场所。（个别配用YB系列电动机，则无220V电制）。 CWL series marine small sized centrifugal fans is capable of blowing air, ocean air containing salt vapor, and corrosive air which contains oil vapor. It can be used for ventilation of kitchen, toilet, wardrobe, meeting room and cach cabin, as well as other suitable place land chemical industry and metallurgy. This series fans with Explosion -proof motors can delivered gas mixtures or vapor containing combustibles and explosives, it can run normally at danger field. CWL (CXL) series fans fit with Marine three-phase tiny asynchronous motors. Its power can be 380/220V and 50/60HZ. (For some specific fans with YB series motor, its power can't be 220 V).
特点 Features 2.1具有高压力系数（H>1.4），高流量系数（Q>0.5）和高效率（n>65%）。 2.2重量轻、尺寸小、性能稳定、噪声低。 3.3性能参数多，适用范围广。 3.4强度好、耐腐蚀。 3.5抗摇摆、振动和冲击性能强。 2.1 High parameter of pressure (H>1.4), high parameter of capacities (Q>0. 5), high efficiency (n> 65%), 2.2 Light in weight, small in size, reliable in operation, low noise. 2.3 Performance parameter is various and application field is wide. 2.4 High strength, good anticorrosion. 2.5 Strong resistance against swing, vibration and impact.
工作原理和机构形式 Working principle and structure type CWL (CXL)系列舰船小型离心通风机，是一种新顺的高性能节能风机，采用船用三相微型异步电动机。风机叶轮由强烈前向多翼式叶片组成，气体从轴向进入叶片通道，在离心力的作用下产生能量，气体被压缩并从径向输入管路。 CWL (CXL)型风机为卧式，电动机直联式结构，外可制成置式结构。-轮为制我而成，机壳和进风口均为焊接结构。 叶轮必须经静、动平衡样正（采用加重法）。 通风机可制成（左转）或（右转）两种。 The CWL (CXL) series marine small centrifugal fan are a kind of high efficiently fans. They are equipped with marine three phase tiny asynchronous motors. The impellers of fans are consisting of strong foreword poly blades. The air enter the blade-passage from axial direction and produce energy by the centrifugal force, it is compressed and enter the pipeline from radial direction. The CWL (CXL) type fan is horizontal structure type, the impeller is mounted directly on the motor shaft. The impeller is rivet jointed structure and the casing and entrance are welded structure. The impeller must be correct by static and dynamic balance(adopted the method of adding weight:) The fan can be made for left or right rotation.
型号说明Model explanation C W L - 160D（G） 叶轮直径为100mm，D为低速（G为高速） impeller diameter is100mm，D is low speed （G is high speed) 离心风机centrifugal tan 小型small-sized 舰船用marine or navy
型号 Model | 流量 Flow rate m3/h | 全压 Total Pressure Pa | 静压 Static pressure Pa | 转速 Speed r/min | 声压级 SOundpressoue level dB(A) | 电动机 Motor |  |  | 外形尺寸 | [26 empty] | 重量 weight kg
Dimensions
[6 empty] | 频率 Freq Hz | 功率 Power KW | 型号 Model | A | A1 | A2 | B | B1 | B2 | B3 | D1 | D2 | D3 | nxdl |  | nxdl |  | H | h | h1 | h2 | M | M1 | L | L1 | L2 | L3 | L4 | 4-K
CWL-100D | 110 | 90 | 67 | 1400 | 52 | 50 | 0.12 | Y631-4-H | 64 | 98 | 84 | 76 | 108 | 94 | 50 | Ф119 | Ф104 | Ф86 | 6 | Ф6 | 6 | Ф6 | 192 | 63 | 76 | 62 | 163.5 | 75 | 280 | 56 | 74 | 80 | 90 | 4 | Ф7 | 13.5
| 135 | 133 | 99 | 1700 | 55 | 60 | 0.12
CWL-100G | 220 | 360 | 268 | 2800 | 63 | 50 | 0.18 | Y631-2-H
| 270 | 532 | 396 | 3400 | 67 | 60 | 0.18
CWL-110D | 150 | 110 | 80 | 1400 | 54 | 50 | 0.12 | Y631-4-H | 70 | 104 | 90 | 84 | 116 | 102 | 55 | Ф128 | Ф113 | Ф95 | 6 | Ф6 | 6 | Ф6 | 209.5 | 63 | 83.5 | 68 | 180 | 82.5 | 290 | 61.5 | 77 | 80 | 100 | 4 | Ф7 | 13.5
| 185 | 162 | 118 | 1700 | 58 | 60 | 0.12
CWL-110G | 300 | 440 | 320 | 2800 | 65 | 50 | 0.18 | Y631-2-H
| 370 | 648 | 472 | 3400 | 69 | 60 | 0.18
CWL-125D | 220 | 140 | 102 | 1400 | 57 | 50 | 0.12 | Y631-4-H | 80 | 114 | 100 | 95 | 127 | 113 | 62.5 | Ф141 | Ф126 | Ф108 | 6 | Ф6 | 6 | Ф6 | 236 | 63 | 95 | 78 | 205 | 94 | 301 | 68.5 | 82.5 | 80 | 100 | 4 | Ф7 | 15.5
| 270 | 206 | 150 | 1700 | 61 | 60 | 0.12
CWL-125G | 440 | 560 | 408 | 2800 | 69.5 | 50 | 0.18 | Y631-2-H
| 540 | 824 | 600 | 3400 | 72 | 60 | 0.18
CWL-140D | 300 | 180 | 135 | 1400 | 60 | 50 | 0.12 | Y631-4-H | 90 | 134 | 114 | 107 | 149 | 129 | 70 | Ф164 | Ф144 | Ф121 | 6 | Ф7 | 6 | Ф7 | 267 | 63 | 106 | 86.5 | 228.5 | 105 | 315 | 77.5 | 87.5 | 80 | 100 | 4 | Ф7 | 19
| 365 | 265 | 199 | 1700 | 64 | 60 | 0.12
CWL-140G | 600 | 720 | 540 | 2800 | 71.5 | 50 | 0.25 | Y632-2-H | [15 empty] | 71 |  |  |  |  | 350 |  | 92.5 | 90 | 112 | 4 | Ф7 | 21
| 730 | 1060 | 796 | 3400 | 76 | 60 | 0.37 | Y712-2-H
CWL-160D | 450 | 230 | 170 | 1400 | 64 | 50 | 0.12 | Y631-4-H | 102 | 146 | 126 | 122 | 165 | 145 | 80 | Ф181 | Ф161 | Ф138 | 6 | Ф7 | 6 | Ф7 | 303 | 63 | 121.5 | 99 | 261.5 | 120 | 346 | 86 | 93.5 | 80 | 100 | 4 | Ф7 | 20
| 550 | 339 | 251 | 1700 | 68 | 60 | 0.12
CWL-160G | 900 | 920 | 680 | 2800 | 75 | 50 | 0.37 | Y712-2-H | [15 empty] | 71 |  |  |  |  | 364 |  | 98 | 90 | 112 | 4 | Ф7 | 22
| 1100 | 1356 | 1004 | 3500 | 79 | 60 | 0.75 | Y801-2-H | [15 empty] | 80 |  |  |  |  | 394 |  | 103 | 100 | 125 | 4 | Ф10 | 26
CWL-180D | 640 | 290 | 217 | 1400 | 67 | 50 | 0.37 | Y712-4-H | 115 | 171 | 146 | 137 | 190 | 165 | 90 | Ф208 | Ф183 | Ф155 | 6 | Ф9 | 6 | Ф9 | 343 | 71 | 130.5 | 111.5 | 294 | 135 | 382 | 96.5 | 106 | 90 | 112 | 4 | Ф7 | 23
| 780 | 428 | 320 | 1700 | 71 | 60 | 0.37
CWL-180G | 1280 | 1160 | 868 | 2920 | 78 | 50 | 0.75 | Y801-2-H | [15 empty] | 80 |  |  |  |  | 412 |  | 111 | 100 | 125 | 4 | Ф10 | 27
| 1600 | 1812 | 1356 | 3400 | 82.5 | 60 | 1.5 | Y90S-2-H | [15 empty] | 90 |  |  |  |  | 427 |  | 117 | 100 | 125 | 4 | Ф10 | 30
CWL-200D | 900 | 375 | 276 | 1460 | 70 | 50 | 0.55 | Y801-4-H | 128 | 184 | 159 | 152 | 205 | 180 | 100 | Ф225 | Ф200 | Ф172 | 6 | Ф9 | 6 | Ф9 | 378 | 80 | 151.5 | 124 | 306.5 | 150 | 427 | 104.5 | 117 | 100 | 125 | 4 | Ф10 | 30
| 1080 | 553 | 407 | 1750 | 74 | 60 | 0.55
CWL-200G | 1880 | 1631 | 1201 | 2800 | 82 | 50 | 1.5 | Y90S-2-H | [15 empty] | 90 |  |  |  |  | 442 |  | 123 | 125 | 140 | 4 | Ф10 | 43
| 2250 | 2343 | 1725 | 3400 | 85 | 60 | 2.2 | Y90L-2-H | [20 empty] | 467 | [6 empty] | 45