## Sheet1
CGDL系列舰船用高效率低噪声离心通机
CGDL series marine high efficiency low-noise centrifhgal fans
概述 General CGDL系列舰船用高效率低噪声离心通风机（以下简称通风机）是一种新型节能、低噪声舰船用产品。通风机通过专门设计和加工，具有效率高（n>80%）、噪声低、不会超载、运转平稳和满足舰船条件要求等特点，它适用于各种舰船的通风换气，也适用于其它相适应的场合。 CGDL Series marine or navy high-efficiency, low-noise centrifugal fans (thereafter called the fan) are new-type & energy- save. By the special design and process, the fans are characterized with high efficiency (n> 80%), low noise, no overload, stable running and meeting the marine conditions etc. They are suitable for chamber ventilation and also applicable for other suitable places.
特点 Features 通风机采用了特殊设计的机翼型叶片和进风口。机壳的尺寸和型线也按特征速度进行专门设计。叶轮进行专门加工，从而使气流流动更良好，使通风机里具有效名高、噪音低等优点，由于功率特征至大流量区后反而下降，故电动机不会因超载而损坏。 通风机在设计和制造中充分考虑到舰船用的特殊条件要求，叶轮用铝合金制造并经严格动平衡校正、超速试验。故通风机还具有耐蚀性好、抗摇摆、抗冲击、振动、运转平稳和安全可靠等特点。 The fans are specially designed with aerofoil blade and inlet. The dimension and line of the casing are designed specially according to characteristic speeds. The impeller are processed specially so that air flows perfectly and the fan have the advantages of high efficiency and low noise. When power gets to large flow, it gets down oppositely. Therefore, the motor can not be damaged due to overload. During the course of design & manufacture, we had thought fully of the marine special conditions. The impellers are made of Aluminum with strict dynamic balance & over speed test. Therefore, the fans also have the features of anti corrosion. Resistance swing, shock resistance and vibration resistance, stable turning, safety & reliability etc.
结构型式 structure 通风机为卧式，电动机直联结构，需要时也可制成立式结构。 通风机叶轮由铝合金制成，叶片为机翼型，并经过严格动平衡校正，具有优良的空气性能。机壳、进风口等由普通钢板制成，采用镀锌等防腐措施，机号≥40时，通风机加有机架（40以下无机架）。 通风级号40~80的风口方向在0~225°按22.5°变化。 The fans are horizontal with motor direct coupling. However it can also be constructed into a vertical type. The impellers are aluminum alloy and blades are aerofoil. They are adjusted strictly by dynamic balance, so that they have good air dynamic performance. The casing and inlet are made by common galvanized steel sheet. When the machine number is ≥40, the fans have frame. The outlet directions of No.40-80 of the fans are 0~225。and change by 22.5。.
型号说明 Model explanation C G D L - 40 -4 4极电机4poles motor 叶轮直径40cm（圆整）impeller diameter is 40cm 离心风机centrifugal fan 低噪声low noise 高效率high efficieney 舰船用marine or navy
型号Model | 流量 | 全压 | 静压 | 转速 | 噪声 | 电动机Motor |  |  | 外形尺寸Dimensions
| Flow rate | Total Pressure | Static pressure | Speed | Noise | 频率 Freq Hz | 功率 Power KW | 型号 Model | A | B | A1 | A2 | B1 | B2 | D0 | D1 | D2 | n1*Ф1 | n2×Ф2 | n3×Ф3 | M1 | M2 | M3 | L1 | L2 | L3 | L4 | L5 | h | h1 | h2 | M | H | L | 重量 Weight kg
| m3/h | Pa | Pa | r/min | dB(A)
CGDL-20-2 | 400 | 570(58) | 550(56) | 2920 | 63 | 50 | 0.37 | Y7112-H | 120 | 150 | 76*2 | 175 | 60*2 | 203 | Ф170 | Ф200 | Ф224 | 10*Ф8 | 8×Ф8 | 4×Ф8 | 156.5 | 112 | 145 | 105 |  | 112 | 90 |  | 105 | 141 | 71 | 318 | 348 | 398 | 20
| 600 | 500(51) | 450(46) |  | 62
| 800 | 380(39) | 295(30) |  | 63
| 600 | 790(80) | 735 (75) | 3500 | 67 | 60 |  | JY711-2-H
| 800 | 680(69) | 590(60) |  | 67
| 1000 | 440(45) | 390(40) |  | 67
CGDL-25-2 | 800 | 790(80) | 745(76) | 2920 | 68 | 50 | 0.55 | Y7112-H | 155 | 185 | 93*2 | 210 | 72*3 | 238 | Ф210 | Ф240 | Ф264 | 10*Ф8 | 8×Ф8 | 4×Ф8 | 181.5 | 112 | 145 | 125 |  | 129 | 90 |  | 124 | 170 | 71 | 375 | 412 | 436 | 25
| 1100 | 700(71) | 630(64) |  | 67
| 1500 | 540(55) | 410(42) |  | 68
| 1000 | 1140(116) | 1060 (108) | 3500 | 72 | 60 |  | JY712-2-H
| 1400 | 990(101) | 880(89) |  | 72
| 1800 | 775(79) | 590(60) |  | 73
CGDL-28-2 | 1000 | 970(99) | 940(96) | 2920 | 71 | 50 | 0.75 | Y801-2-H | 180 | 215 | 106*2 | 235 | 82*3 | 268 | Ф240 | Ф270 | Ф294 | 10*Ф8 | 8×Ф8 | 4×Ф10 | 201.5 | 125 | 160 | 138 |  | 146 | 100 |  | 140 | 193 | 80 | 422 | 466 | 477 | 38
| 1600 | 860(88) | 790(80) |  | 71
| 2200 | 650(66) | 500(51) |  | 72
| 1200 | 1390(141) | 1350(137) | 3500 | 74 | 60 | 1.1 | JY801-2-H
| 1900 | 1230(125) | 1130(115) |  | 74
| 2600 | 930(94) | 720(73) |  | 75
CGDL-32-2 | 1600 | 1320(135) | 1280(130) | 2920 | 75 | 50 | 1.1 | JY802-2-H | 210 | 245 | 124*2 | 276 | 94*3 | 309 | Ф270 | Ф305 | Ф335 | 10*Ф10 | 8×Ф10 | 4×Ф10 | 225 | 125 | 160 | 160 |  | 163 | 100 |  | 159 | 218 | 80 | 476 | 532 | 515 | 48
| 2200 | 1220(124) | 1130(115) |  | 75
| 3000 | 940(96) | 790(80) |  | 76
| 1900 | 1890(191) | 1830(185) | 3500 | 78 | 60 | 2.2 | JY90L-2-H | [13 empty] | 140 | 176 |  |  | 169 | 125 |  |  |  | 90 |  |  | 607 | 53
| 2600 | 1750(177) | 1620(164) |  | 79
| 3600 | 1350(137) | 1130(115) |  | 80
CGDL-32-4 | 900 | 330(34) | 310(32) | 1460 | 62 | 50 | 0.55 | Y801-4-H | 210 | 245 | 124*2 | 276 | 94*3 | 309 | Ф270 | Ф305 | Ф335 | 10*Ф10 | 8×Ф10 | 4×Ф10 | 225 | 125 | 160 | 160 |  | 163 | 100 |  | 159 | 218 | 80 | 476 | 532 | 515 | 48
| 1200 | 290(30) | 260(27) |  | 62
| 1500 | 235(24) | 195(20) |  | 63
| 1000 | 470(48) | 450(46) | 1750 | 65 | 60 |  | JY801-4-H
| 1400 | 420(43) | 390(40) |  | 65
| 1800 | 340(35) | 280(29) |  | 66
CGDL-36-2 | 2400 | 1690(172) | 1620(165) | 2920 | 80 | 50 | 2.2 | Y90L-2-H | 230 | 280 | 134*2 | 296 | 105*3 | 344 | Ф320 | Ф355 | Ф385 | 10*Ф10 | 8×Ф10 | 4×Ф10 | 252 | 140 | 176 | 170 |  | 179 | 125 |  | 176 | 249 | 90 | 534 | 595 | 596 | 60
| 3300 | 1550(158) | 1430(146) |  | 79
| 4200 | 1320(135) | 1130(115) |  | 80
| 2850 | 2420(244) | 2320(234) | 3500 | 83 | 60 | 4 | JY90L-2-H | [13 empty] | 190 | 240 |  |  | 181 | 140 |  |  |  | 112 |  |  | 636 | 80
| 3950 | 2220(224) | 2050(207) |  | 82
| 6000 | 1890(191) | 1620(164) |  | 83
CGDL-36-4 | 1400 | 410 (42) | 390(40) | 1460 | 64 | 50 | 0.55 | Y80L-4-H | 230 | 280 | 134*2 | 296 | 105*3 | 344 | Ф320 | Ф355 | Ф385 | 10*Ф10 |  |  |  | 125 | 160 |  |  | 173 | 100 |  |  |  | 80 |  |  | 534 | 50
| 1800 | 380(39) | 350(36) |  | 64
| 2200 | 300(31) | 245(25) |  | 65
| 1400 | 610(62) | 590(60) | 1750 | 69 | 60 |  | JY80L-4-H
| 1900 | 580(59) | 530(54) |  | 68
| 2500 | 490(50) | 420(43) |  | 69
型号Model | 流量 | 全压 | 静压 | 转速 | 噪声 | 电动机Motor |  |  | 外形尺寸Dimensions
| Flow rate | Total Pressure | Static pressure | Speed | Noise | 频率 Freq Hz | 功率 Power KW | 型号 Model | A | B | A1 | A2 | B1 | B2 | D0 | D1 | D2 | n1*Ф1 | n2×Ф2 | n3×Ф3 | M1 | M2 | M3 | L1 | L2 | L3 | L4 | L5 | h | h1 | h2 | M | H | L | Weight
| m3/h | Pa | Pa | r/min | dB(A) | [29 empty] | kg
CGDL-40-2 | 4000 | 2160 (220) | 2040(208) | 2920 | 83 | 50 | 4 | Y112M-2-H | 255 | 310 | 146*2 | 321 | 115*3 | 374 | Ф 360 | Ф 395 | Ф 425 | 10*Ф 10 | 8×Ф10 | 6×Ф12 | 282 | 310 | 344 | 182 | 100 | 175 | 190 | 580 | 191 | 302 | 112 | 594 | 680 | 660 | 100
| 5500 | 1860(190) | 1640(167) |  | 83
| 7000 | 1420(145) | 1060(108) |  | 84 |  |  | JY112M-2-H
CGDL-40-4 | 2000 | 530(54) | 500(51) | 1400 | 68 | 50 | 0.75 | Y802-4-H | [18 empty] | 120 | 500 |  |  | 80 |  |  | 560 | 71
| 2800 | 470(48) | 410(42) |  | 68
| 3500 | 370(38) | 280(29) |  | 69 |  |  | JY802-4-H
| 2400 | 760(78) | 725 (74) | 1750 | 72 | 60 | 1.1 | Y90S-4-H | [22 empty] | 90 |  |  | 586 | 75
| 3200 | 700(71) | 620(63) |  | 72
| 4200 | 540(55) | 410(42) |  | 73 |  |  | JY90S-4-H
CGDL-45-2 | 5000 | 2960 (302) | 2840(290) | 2920 | 88 | 50 | 7.5 | Y132S2-2-H | 290 | 345 | 109*3 | 356 | 127*3 | 409 | Ф 400 | Ф 435 | Ф 465 | 12*Ф 10 | 12×Ф10 | 6×Ф12 | 310 | 350 | 384 | 200 | 110 | 200 | 200 | 660 | 214 | 334 | 132 | 658 | 752 | 740 | 141
| 7000 | 2580(263) | 2350(240) |  | 87
| 9000 | 1940(198) | 1570(160) |  | 88 |  |  | JY132S2-2-H
CGDL-45-4 | 2400 | 755(77) | 725(74) | 1460 | 72 | 50 | 1.1 | Y90S-4-H | [18 empty] | 120 | 550 |  |  | 90 |  |  | 621 | 90
| 3600 | 610(62) | 540(55) |  | 72
| 5000 | 410(42) | 290(30) |  | 73 |  |  | JY90S-4-H
| 3000 | 1060(108) | 1020 (104) | 1750 | 76 | 60 | 1.5 | Y90L-4-H | [25 empty] | 666
| 4500 | 870(89) | 775(79) |  | 76
| 6000 | 590(60) | 420(43) |  | 77 |  |  | JY90L-4-H
CGDL-50-2 | 8000 | 3320 (339) | 3130(320) | 2920 | 91 | 50 | 15 | Y160M2-2-H | 320 | 390 | 119*3 | 386 | 142*3 | 455 | Ф 450 | Ф 485 | Ф 515 | 12*Ф 10 | 12×Ф10 | 4×Ф15 | 338 | 254 | 330 | 215 |  | 227 | 210 |  | 240 | 345 | 160 | 729 | 812 | 880 | 224
| 10000 | 2030(310) | 2740(280) |  | 90
| 12000 | 2450(250) | 2040(208) |  | 91 |  |  | JY1160M2-2-H
CGDL-50-4 | 4000 | 830(85) | 790(80) | 1460 | 75 | 50 | 1.5 | Y90L-4-H | [11 empty] | 6×Ф12 | 338 | 390 | 429 | 215 | 125 | 220 | 130 | 600 |  | 370 | 90 |  | 837 | 681 | 110
| 5000 | 760(78) | 690(70) |  | 75
| 6000 | 620(63) | 510(52) |  | 75 |  |  | JY90L-4-H
| 4500 | 1220(124) | 1160 (118) | 1750 | 79 | 60 | 3 | Y100L2-4-H | [22 empty] | 100 |  |  | 706 | 113
| 6000 | 1090(111) | 980(100) |  | 79
| 7500 | 755(77) | 590(60) |  | 79 |  |  | JY100L2-4-H
CGDL-55-4 | 4500 | 1010(103) | 970(99) | 1460 | 77 | 50 | 2.2 | Y100L1-4-H | 355 | 425 | 131*3 | 423 | 154*3 | 491 | Ф 490 | Ф 532 | Ф 566 | 12*Ф 10 | 12×Ф10 | 6×Ф12 | 367 | 416 | 456 | 240 | 140 | 240 | 160 | 670 | 260 | 400 | 100 | 795 | 905 | 742 | 180
| 6400 | 880(90) | 800(82) |  | 77
| 8400 | 690(70) | 540(55) |  | 78 |  |  | JY100L1-4-H
| 5400 | 1450(148) | 1390(142) | 1750 | 81 |  | 4 | Y112M4-4-H | [22 empty] | 112 |  |  | 760 | 184
| 7800 | 1260(128) | 1130(115) |  | 81
| 10500 | 930(95) | 710(72) |  | 82 |  |  | JY112M-4-H
CGDL-55-6 | 3400 | 420(43) | 400(41) | 970 | 68 | 50 | 0.75 | Y90S-6-H | [18 empty] | 120 | 620 |  |  | 90 |  |  | 695 | 175
| 4200 | 390(40) | 350(36) |  | 68
| 5400 | 320(33) | 260(27) |  | 69 |  |  | JY90S-6-H
| 4000 | 610(62) | 580(59) | 1160 | 72 | 60 | 1.1 | Y90L-6-H | [25 empty] | 740
| 5000 | 560(57) | 510(52) |  | 72
| 6400 | 450(46) | 380(37) |  | 73 |  |  | JY90L-6-H
CGDL-60-4 | 5400 | 1180 (120) | 1130 (115) | 1460 | 79 | 50 | 3 | Y100L2-4-H JY100L2-4-H | 380 | 460 | 142*3 | 458 | 167*3 | 536 | Ф 530 | Ф 572 | Ф 606 | 12*Ф 12 | 16×Ф10 | 6×Ф15 | 390 | 462 | 506 | 254 | 155 | 250 | 170 | 710 | 280 | 427 | 100 | 847 | 975 | 768 | 270
| 7600 | 1050(107) | 960(98) |  | 79
| 9500 | 790(80) | 650(66) |  | 79
| 6500 | 1690 (172) | 1620 (165) | 1750 | 84 |  | 5.5 | Y132S-4-H JY132S-4-H | [22 empty] | 132 |  |  | 840 | 274
| 9000 | 1540(157) | 1410(144) |  | 83
| 12000 | 1040(106) | 820(84) |  | 84
CGDL-60-6 | 4500 | 470(48) | 440(45) | 970 | 79 | 50 | 1.1 | Y90L-6-H JY90L-6-H | [18 empty] | 140 | 680 |  |  | 90 |  |  | 756 | 261
| 5600 | 410(42) | 360(37) |  | 70
| 6500 | 310(32) | 240(25) |  | 71
| 4500 | 710(72) | 680 (69) | 1160 | 74 | 60 | 1.5 | Y100L-6-H JY100L-6-H | [22 empty] | 100 |  |  | 768 | 259
| 6000 | 640(65) | 580(59) |  | 74
| 7800 | 430(44) | 340(35) |  | 75
CGDL-70-4 | 9000 | 1730 (176) | 1670(170) | 1460 | 86 | 50 | 11 | Y160M-4-H | 450 | 545 | 165*3 | 528 | 147*4 | 621 | Ф 620 | Ф 662 | Ф 696 | 14*Ф 12 | 16×Ф12 | 6×Ф15 | 465 | 542 | 586 | 290 | 190 | 290 | 280 | 930 | 327 | 507 | 160 | 1007 | 1114 | 1012 | 330
| 11000 | 1700(174) | 1610(164) |  | 85
| 14000 | 1570(160) | 1420(145) |  | 85 |  |  | JY160M-4-H
| 17000 | 1320(135) | 1100(112) |  | 86
CGDL-70-6 | 7000 | 755(77) | 715(73) | 970 | 76 | 50 | 3 | Y132S-6-H JY132S-6-H | [18 empty] | 210 | 830
| 9000 | 700(71) | 640(65) |  | 76
| 11000 | 610(62) | 510(52) |  | 78
| 8000 | 1090(111) | 1040 (106) | 1160 | 80 | 60 | 4 | Y132M1-6-H JY132M1-6-H | [22 empty] | 132 |  |  | 912 | 251
| 10000 | 1030(105) | 950(97) |  | 80
| 13000 | 850(87) | 720(74) |  | 82 | [28 empty] | 950
CGDL-80-4 | 14000 | 2030 (207) | 1940(198) | 1460 | 90 | 50 | 15 | Y160L-4-H JY160L-4-H | 510 | 620 | 139*4 | 588 | 166*4 | 696 | Ф700 | Ф 742 | Ф 776 | 16*Ф 12 | 16×Ф12 | 6×Ф19 | 509 | 590 | 644 | 320 | 210 | 320 | 300 | 980 | 370 | 564 | 160 | 1120 | 1282 | 1126 | 362
| 18000 | 1910(195) | 1760(180) |  | 89
| 21000 | 1640(167) | 1430(146) |  | 88
| 24000 | 1320(135) | 1060(108) |  | 88
CGDL-80-6 | 9000 | 920(94) | 880(90) | 970 | 79 | 50 | 4 | Y132M1-6-H JY132M1-6-H | [18 empty] | 240 | 930 |  |  | 132 |  |  | 1010 | 300
| 12500 | 830(85) | 760(78) |  | 79
| 16000 | 590(60) | 470(48) |  | 80
| 9000 | 13300(136) | 1290 (132) | 1160 | 83 | 60 | 7.5 | Y160M-6-H JY160M-6-H | [18 empty] | 300 | 980 |  |  | 160 |  |  | 1172 | 362
| 12000 | 1290(132) | 1230(125) |  | 83
| 15000 | 1190(121) | 1080(110) |  | 84
| 19000 | 850(87) | 690(70) |  | 84